## Sheet1
Full Tag Name | Main Equipment | Unique Number | Colloquial Name | Element Type | PLC Tag | UDT Type | Data Type | Units | Raw Min | Raw Max | EU Min | EU Max
FS-ZIT-0324 | 03 | 24 | Charge Ram Position | Instrument | FS_ZIT_0324 | AI | AI | in | 4000 | 20000 | 0 | 180
CAI-MCZ-0601 | 06 | 01 | Primary Burner Blower | VFD | CAI_MCZ_0601 |  | EtherNet/IP
CAI-MCZ-0603 | 06 | 03 | Underfire/Sidefire Blower | VFD | CAI_MCZ_0603 |  | EtherNet/IP
CAI-PSLL-0612 | 06 | 12 | Primary Gas Low Low | Pressure Switch | CAI_PSLL_0612 | DI | DI
CAI-PSHH-0616 | 06 | 16 | Primary Gas High High | Pressure Switch | CAI_PSHH_0616 | DI | DI
CAI-PSLL-0619 | 06 | 19 | Primary Air Low Low | Pressure Switch | CAI_PSLL_0619 | DI | DI
CAI-ZIT-0664 | 06 | 64 | Upper Ram Position | Instrument | CAI_ZIT_0664 | AI | AI | in | 4000 | 20000 | 0 | 180
CAI-ZIT-0674 | 06 | 74 | Lower Ram Position | Instrument | CAI_ZIT_0674 | AI | AI | in | 4000 | 20000 | 0 | 180
CAI-PDT-0688A | 06 | 88 | Sidefire Air Flow A | Instrument | CAI_PDT_0688A | AI | AI |  | 4000 | 20000 | 0 | 10
CAI-PDT-0688B | 06 | 88 | Sidefire Air Flow B | Instrument | CAI_PDT_0688B | AI | AI |  | 4000 | 20000 | 0 | 10
CAI-PDT-0689A | 06 | 89 | Underfire Air Flow A | Instrument | CAI_PDT_0689A | AI | AI |  | 4000 | 20000 | 0 | 10
CAI-PDT-0689B | 06 | 89 | Underfire Air Flow B | Instrument | CAI_PDT_0689B | AI | AI |  | 4000 | 20000 | 0 | 10
CAI-PDT-0689C | 06 | 89 | Underfire Air Flow C | Instrument | CAI_PDT_0689C | AI | AI |  | 4000 | 20000 | 0 | 10
CAI-PDT-0689D | 06 | 89 | Underfire Air Flow D | Instrument | CAI_PDT_0689D | AI | AI |  | 4000 | 20000 | 0 | 10
CAI-TAI-0698 | 06 | 98 | Primary Chamber Temp | Instrument | CAI_TAI_0698 | TAI | AI | °F | 4000 | 20000 | 0 | 2500
CAI-PIT-0699 | 06 | 99 | Primary Chamber Draft | Instrument | CAI_PIT_0699 | AI | AI |  | 4000 | 20000 | -4 | 4
CAI-MCZ-0901 | 09 | 01 | Secondary Burner Blower | VFD | CAI_MCZ_0901 |  | EtherNet/IP
CAI-MCZ-0902 | 09 | 02 | Flameport Blower | VFD | CAI_MCZ_0902 |  | EtherNet/IP
CAI-PSLL-0904 | 09 | 04 | Secondary Air Low Low | Pressure Switch | CAI_PSLL_0904 | DI | DI
CAI-PSLL-0912 | 09 | 12 | Secondary Gas Low Low | Pressure Switch | CAI_PSLL_0912 | DI | DI
CAI-PSHH-0916 | 09 | 16 | Secondary Gas High High | Pressure Switch | CAI_PSHH_0916 | DI | DI
APC-AIT-0988 | 09 | 88 | Exhaust Oxygen Level | Instrument | APC_AIT_0988 | AI | AI | % | 4000 | 20000 | 0 | 21
CAI-TAI-0998 | 09 | 98 | Secondary Chamber Temp | Instrument | CAI_TAI_0998 | TAI | AI | °F | 4000 | 20000 | 0 | 2500
APC-PIT-1221 | 12 | 21 | Emergency Bypass Press | Instrument | APC_PIT_1221 | AI | AI | psig | 4000 | 20000 | 0 | 150
APC-TAI-1298 | 12 | 98 | Emergency Bypass Temp | Instrument | APC_TAI_1298 | TAI | AI | °F | 4000 | 20000 | 0 | 2500
AUX-FIT-1506 | 15 | 06 | SNCR Reagent Flow | Instrument | AUX_FIT_1506 | AI | AI | gph | 4000 | 20000 | 0 | 6
APC-FIT-2108 | 21 | 08 | Prequench Water Flowrate | Instrument | APC_FIT_2108 | AI | AI | gpm | 4000 | 20000 | 0 | 18
APC-PSLL-2172 | 21 | 72 | PreQuench Air Low Low | Pressure Switch | APC_PSLL_2172 | DI | DI
APC-TAI-2198 | 21 | 98 | Prequench Temp | Instrument | APC_TAI_2198 | TAI | AI | °F | 4000 | 20000 | 0 | 2500
APC-MC-2401A | 24 | 01 | PEC Makeup Water Pump A | E1+ | APC_MC_2401A |  | EtherNet/IP
APC-MC-2401B | 24 | 01 | PEC Makeup Water Pump B | E1+ | APC_MC_2401B |  | EtherNet/IP
APC-MC-2403A | 24 | 03 | PEC Brine Pump A | E1+ | APC_MC_2403A |  | EtherNet/IP
APC-MC-2403B | 24 | 03 | PEC Brine Pump B | E1+ | APC_MC_2403B |  | EtherNet/IP
APC-FIT-2408 | 24 | 08 | PEC Freshwater Flowrate | Instrument | APC_FIT_2408 | AI | AI | gpm | 4000 | 20000 | 0 | 18
APC-FIT-2428 | 24 | 28 | PEC Brine Flowrate | Instrument | APC_FIT_2428 | AI | AI | gpm | 4000 | 20000 | 0 | 200
APC-LT-2441 | 24 | 41 | PEC Sump Level | Instrument | APC_LT_2441 | AI | AI |  | 4000 | 20000
APC-ZIT-2451 | 24 | 51 | PEC Water Valve | Instrument | APC_ZIT_2451 | AI | AI | % | 4000 | 20000 | 0 | 100
APC-AIT-2488 | 24 | 88 | PEC Brine pH | Instrument | APC_AIT_2488 | AI | AI | pH | 4000 | 20000 | 0 | 14
APC-TAI-2498 | 24 | 98 | PEC Outlet Temp | Instrument | APC_TAI_2498 | TAI | AI | °F | 4000 | 20000 | 0 | 2500
APC-MC-2701A | 27 | 01 | AGR Brine Pump A | E1+ | APC_MC_2701A |  | EtherNet/IP
APC-MC-2701B | 27 | 01 | AGR Brine Pump B | E1+ | APC_MC_2701B |  | EtherNet/IP
APC-PIT-2707 | 27 | 07 | AGR Outlet Press | Instrument | APC_PIT_2707 | AI | AI | in wc | 4000 | 20000 | -4 | 4
APC-TAI-2723 | 27 | 23 | AGR Brine Temp | Instrument | APC_TAI_2723 | TAI | AI | °F | 4000 | 20000 | 0 | 2500
APC-FIT-2728 | 27 | 28 | AGR Brine Flowrate | Instrument | APC_FIT_2728 | AI | AI | gpm | 4000 | 20000 | 0 | 300
APC-LSLL-2741 | 27 | 41 | AGR Sump Level Low Low | Level Switch | APC_LSLL_2741 | DI | DI
APC-AIT-2788 | 27 | 88 | AGR Brine pH | Instrument | APC_AIT_2788 | AI | AI | pH | 4000 | 20000 | 0 | 14
APC-TAI-2798 | 27 | 98 | AGR Outlet Temp | Instrument | APC_TAI_2798 | TAI | AI | °F | 4000 | 20000 | 0 | 2500
APC-MC-3001A | 30 | 01 | PR Venturi Brine Pump A | E1+ | APC_MC_3001A |  | EtherNet/IP
APC-MC-3001B | 30 | 01 | PR Venturi Brine Pump B | E1+ | APC_MC_3001B |  | EtherNet/IP
APC-PDIT-3007 | 30 | 07 | PR Venturi dP | Instrument | APC_PDIT_3007 | AI | AI | in wc | 4000 | 20000 | 0 | 80
APC-TAI-3023 | 30 | 23 | PR Brine Temp | Instrument | APC_TAI_3023 | TAI | AI | °F | 4000 | 20000 | 0 | 2500
APC-FT-3028 | 30 | 28 | PR Brine Flowrate | Instrument | APC_FT_3028 | AI | AI |  | 4000 | 20000
APC-ZIT-3051 | 30 | 51 | PR Brine Valve | Instrument | APC_ZIT_3051 | AI | AI | % | 4000 | 20000 | 0 | 100
APC-ZIT-3901 | 39 | 01 | Demister Fill Valve | Instrument | APC_ZIT_3901 | AI | AI | % | 4000 | 20000 | 0 | 100
APC-FIT-3902 | 39 | 02 | Demister Makeup Flowrate | Instrument | APC_FIT_3902 | AI | AI | gpm | 4000 | 20000 | 0 | 18
APC-PDIT-3907 | 39 | 07 | Demister dP | Instrument | APC_PDIT_3907 | AI | AI | in wc | 4000 | 20000 | -4 | 4
APC-MCZ-4800 | 48 | 00 | ID Fan | VFD | APC_MCZ_4800 |  | EtherNet/IP
APC-VT-4801 | 48 | 01 | ID Fan Vibration | Instrument | APC_VT_4801 | AI | AI | in/sec | 4000 | 20000 | 0 | 1
APC-PIT-4807 | 48 | 07 | ID Fan Inlet Press | Instrument | APC_PIT_4807 | AI | AI | in wc | 4000 | 20000 | -80 | 0
APC-TAI-4898 | 48 | 98 | ID Fan Inlet Temp | Instrument | APC_TAI_4898 | TAI | AI | °F | 4000 | 20000 | 0 | 2500
APC-PDIT-4901 | 49 | 01 | Carbon Bed 1 dP | Instrument | APC_PDIT_4901 | AI | AI |  | 4000 | 20000
APC-PDIT-4902 | 49 | 02 | Carbon Bed 2 dP | Instrument | APC_PDIT_4902 | AI | AI |  | 4000 | 20000
APC-PDIT-4903 | 49 | 03 | Carbon Bed Filter dP | Instrument | APC_PDIT_4903 | AI | AI |  | 4000 | 20000
APC-PIT-4910 | 49 | 10 | Carbon Bed Inlet Press | Instrument | APC_PIT_4910 | AI | AI | in wc | 4000 | 20000 | -4 | 4
APC-TAI-4998 | 49 | 98 | Carbon Bed Inlet Temp | Instrument | APC_TAI_4998 | TAI | AI | °F | 4000 | 20000 | 0 | 2500
APC-TAI-4999 | 49 | 99 | Carbon Bed Outlet Temp | Instrument | APC_TAI_4999 | TAI | AI | °F | 4000 | 20000 | 0 | 2500
APC-MCZ-5300 | 53 | 00 | Booster Fan | VFD | APC_MCZ_5300 |  | EtherNet/IP
CAI-MC-5702 | 57 | 02 | Ash Hydraulic Pump | E1+ | CAI_MC_5702 |  | EtherNet/IP
CAI-LSLL-5764 | 57 | 64 | Ash Hyd Fluid Low Low | Level Switch | CAI_LSLL_5764 | DI | DI
CAI-LIT-5798 | 57 | 98 | Ash Sump Level | Instrument | CAI_LIT_5798 | AI | AI |  | 4000 | 20000
AUX-PIT-6123 | 61 | 23 | Water Main Press | Instrument | AUX_PIT_6123 | AI | AI | psig | 4000 | 20000 | 0 | 150
AUX-MCZ-6201 | 62 | 01 | Cooling Tower Blower | VFD | AUX_MCZ_6201 |  | EtherNet/IP
AUX-LSLL-6202 | 62 | 02 | Cooling Sump Low Low | Level Switch | AUX_LSLL_6202 | DI | DI
AUX-MC-6204A | 62 | 04 | Cooling Water Pump A | E1+ | AUX_MC_6204A |  | EtherNet/IP
AUX-MC-6204B | 62 | 04 | Cooling Water Pump B | E1+ | AUX_MC_6204B |  | EtherNet/IP
AUX-FIT-6207 | 62 | 07 | Cooling Water Flow | Instrument | AUX_FIT_6207 | AI | AI | % | 4000 | 20000 | 0 | 100
AUX-LSL-6208 | 62 | 08 | Cooling Tower Water Low | Level Switch | AUX_LSL_6208 | DI | DI
AUX-AIT-6288 | 62 | 88 | Cooling Water pH | Instrument | AUX_AIT_6288 | AI | AI | pH | 4000 | 20000 | 0 | 14
AUX-AIT-6289 | 62 | 89 | Cooling Water Salinity | Instrument | AUX_AIT_6289 | AI | AI | mS | 4000 | 20000 | 0 | 14
AUX-TAI-6298 | 62 | 98 | Cooling Water Temp | Instrument | AUX_TAI_6298 | TAI | AI | °F | 4000 | 20000 | 0 | 2500
AUX-LIT-6497 | 64 | 97 | Day Tank Level | Instrument | AUX_LIT_6497 | AI | AI | in | 4000 | 20000
AUX-LIT-6498 | 64 | 98 | Main Sump Level | Instrument | AUX_LIT_6498 | AI | AI | in | 4000 | 20000
ELE-ASLL-9050A | 90 | 50 | Main Power Loss A | Analysis Switch | ELE_ASLL_9050A | DI | DI
ELE-ASLL-9050B | 90 | 50 | Main Power Loss B | Analysis Switch | ELE_ASLL_9050B | DI | DI
ELE-ASLL-9070 | 90 | 70 | Controls UPS On Battery | Analysis Switch | ELE_ASLL_9070 | DI | DI
ELE-ASLL-9071 | 90 | 71 | Controls UPS Low Battery | Analysis Switch | ELE_ASLL_9071 | DI | DI
ELE-ASLL-9072 | 90 | 72 | HMI/DAS UPS On Battery | Analysis Switch | ELE_ASLL_9072 | DI | DI
ELE-ASLL-9073 | 90 | 73 | HMI/DAS UPS Low Battery | Analysis Switch | ELE_ASLL_9073 | DI | DI
CAI-MC-9901 | 99 | 01 | Feed Hydraulic Pump | E1+ | CAI_MC_9901 |  | EtherNet/IP
CAI-LSLL-9902 | 99 | 02 | Feed Hyd Fluid Low Low | Level Switch | CAI_LSLL_9902 | DI | DI